## Slide 1
Section 5d
Protection Relay Advanced

## Slide 2: Tripping and Auxiliary Relays
Power system faults are detected by the fault detecting relays, which close their output contacts to initiate tripping. These output contacts are used to energise trip relays and other auxiliary relays which are normally supplied from the station battery d.c. supply.
These auxiliary relays may perform a number of
functions, such as:
• Trip the associated circuit breaker or breakers.
• Send a trip signal to the remote terminal of the line.
• Initiate Auto-reclosing of the circuit breaker.
• Initiate Breaker Failure protection.
• Send a TRIP alarm to the control room operator.

## Slide 3: Circuit Breakers
The circuit breaker is the device that actually interrupts the flow of fault current, and isolates the faulted element (feeder, transformer, etc.) from the remaining healthy components of the power system. The circuit breaker rating must be high enough for it to interrupt the maximum fault current that is possible to flow.

## Slide 4: Circuit Breakers
A typical 230kV circuit breaker rating is 70kA or 25GVA (25,000MVA). As stated earlier, circuit breakers must be capable of interrupting the fault current in very short periods of time. Typical circuit breaker operating times are:
  500 kV - 2 cycles or 40 milli-seconds. (50 Hz system)
  230 kV - 3 cycles or 60 milli-seconds. (50 Hz system)
  33 kV - 6 cycles or 120 milli-seconds. (50 Hz system)